# PRODUCT SPECIFICATION GUIDE

## MODEL: FRONT ACCESS COMBINATION FIRE SMOKE DAMPERS – 3V BLADE

# DIVISION 23 - Heating, Ventilation, and Air Conditioning (HVAC)

1. **GENERAL**
   * + 1. **SECTION INCLUDES**
          1. Front Access combination fire smoke dampers with 3-V blades meeting the requirements of the latest edition of UL Standard 555 and UL Standard 555S.
       2. **SUMMARY**
          1. Section – HVAC Ducts and Casings.
          2. Section – Actuators and Operators.
       3. **REFERENCES**
2. AMCA 500-D – Laboratory Test Methods for Testing Dampers for Ratings.
3. IBC – International Building Code.
4. NFPA 90A - Installation of Air Conditioning and Ventilating Systems.
5. NFPA 92A - Smoke-Control Systems.
6. NFPA 92B – Smoke Control Systems in Atria, Covered Malls, and Large Areas.
7. NFPA 101 – Life Safety Code.
8. UL 555 - Standard for Safety; Fire Dampers.
9. UL 555S - Standard for Safety; Leakage Rated Dampers for Use in Smoke Control Systems.
   * + 1. **SUBMITTALS**
10. Comply with requirements of Submittal Section.
11. Product Data: Submit manufacturer's product data.
    1. Include UL ratings, fire resistance, leakage, velocity, differential pressure, and elevated temperature.
    2. Indicate materials, construction, dimensions, and installation details.
    3. Verify conformance to NFPA, UL, and applicable building code.
    4. Include damper pressure drop data based on tests and procedures performed in accordance with AMCA 500-D.
    5. Include a copy of UL approved installation instructions.
       * 1. **QUALITY ASSURANCE**
            1. Dampers shall be warranted against manufacturing defects for a period of 1 years.
            2. Dampers shall be tested, rated and labeled in accordance with the latest UL-555 and UL-555S requirements
            3. Comply with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems," and with NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."
            4. Damper pressure drop ratings shall be based on tests and procedures performed in accordance with AMCA 500-D.
         2. **DELIVERY, STORAGE, AND HANDLING**
            1. Delivery: Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer, material, and location of installation.
            2. Storage: Store materials in a dry area indoor and protected from damage and in accordance with manufacturer’s instructions.
            3. Handling: Handle and lift dampers by sleeve or frame only. Do not lift damper by blades, actuator, or jackshaft. Protect materials and finishes during handling and installation to prevent damage.
12. **PRODUCTS**
    * + 1. **MANUFACTURER**
           1. Front Access combination fire smoke dampers with 3-V blades shall be in compliance and labelled to UL-555 and UL-555S standard with the specific model reflecting on the UL certificate of the supplier, e.g., Central Ventilation Systems (R27700) and approved by Civil Defense.
        2. **COMBINATION FIRE AND SMOKE DAMPERS**
           1. Model: FSD-3V-FA-21x series Front Access combination fire smoke damper (“x” represents leakage class).
           2. Ratings:

Fire Rating: 1½ hours in accordance with UL-555.

Smoke Rating: Leakage in accordance with UL-555S.

FSD-3V-FA-211 – Leakage Class-1 (8 cfm/ft2 (0.04 m3/ s/m2) at 4 in.wg. (1.0 kPa)

FSD-3V-FA-212 – Leakage Class-2 (20 cfm/ft2 (0.10 m3/ s/m2) at 4 in.wg. (1.0 kPa)

Elevated Temperature Rating: 350ºF (177 ºC)

Air Flow Rating: 2000 fpm (10.2 m/s)

Differential Pressure Rating: 4 in.wg. (1.0 kPa)

* + - * 1. Construction:

Frame: 20-gauge (1mm) Galvanized Roll Formed Steel hat section w/ staked corners for integral bracing. Low profile head and sill on 17 (432 mm) inches high and shorter.

Blades: 16-gauge (1.5mm), 3-V shape, roll formed galvanized steel.

Blade Seals: Silicone rubber permanently bonded to blade.

Jamb Seals: Stainless steel, flexible metal compression type.

Axle Bearings: Bronze oilite press fit into frame.

Axle Material: Plated steel.

Drive Shaft (Jackshaft): ½ inch. (12.7 mm) diameter, plated steel.

Linkage: Plated steel, concealed in frame.

Fire Closure Device: Resettable electric thermostat.

Release Temperature:

* 165 ºF (74 ºC).
* 212 ºF (100 ºC).
* 250 ºF (121 ºC).
* 350 ºF (177 ºC).

Sleeve: Standard 16-inches long x 20-gauge (406mm x 1.0mm), factory installed and wrapped with thermal blanket.

Thermal Blanket: 0.25 inch. (6 mm) thick ceramic fiber of 12 lb/ft3 density, quilted with woven fiberglass fabric, secured with self-tapping screws.

* For Vertical Dampers thermal blanket shall be installed on top and both sides of the sleeve of the FSD-OW or FSD-FA model damper.

Front Access (FA) Panel: Max. 6 inch. (152.4 mm); installed inside damper sleeve to conceal actuators and TRD on the FSD-FA model damper only.

Mounting: Vertical only

Actuator:

Type:

Electric 24V, 50/60 Hz, two-position, fail close.

Electric 230 V, 50/60 Hz, two-position, fail close.

Mounting:

Internal.

* + - 1. **Accessories:**

1. Auxiliary Switch Package for damper open or closed indication:
   * Dual Position Indicator Switch Package: Shall connect directly to the jackshaft and provide full open and full closed blade indication to a remote location.
   * Auxiliary switches to be provided internal to the actuator (recommended)
2. Momentary test switch
3. **EXECUTION**
   * + 1. **EXAMINATION**
          1. Examine areas to receive dampers. Notify the Engineer of conditions that would adversely affect installation or subsequent utilization of dampers. Do not proceed with installation until unsatisfactory conditions are corrected
       2. **INSTALLATION**
          1. Install dampers at locations as indicated on the drawings and in accordance with manufacturer’s UL approved installation instructions.
          2. Install dampers square and free from racking with the blades running horizontally. DO NOT compress or stretch damper sleeve or frame into the duct or opening.
          3. Contractor shall furnish and install duct access door adjacent to dampers for inspection and maintenance. Where duct size permits, install minimum 12 inches x 12 inches (305 x 305 mm) duct access doors.
          4. Handle dampers using the frame or sleeve. Do not lift or move damper using blades, actuator, or jackshaft.
          5. Install bracing as required on multiple section assemblies to support assembly weight and to hold against system pressure.

**END OF SECTION**